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Specification Sheet
Lake Cable Part #: P182C-05CERCO
Description:
18 AWG 2 conductors 7 strands bare copper wire, plenum rated PVC insulation, unshielded, and an overall plenum rated PVC jacket
1. Conductor
1.1. AWG Size & Stranding:
18 AWG 7 Strands Class B
1.2. Material:
Annealed Bare Copper
1.3. Conductor Count:
2 Conductors

2. Insulation
2.1. Material:
Plenum Rated PVC
2.2. Wall Thickness:
0.007”
2.3. Diameter:
0.059” ± 0.002”
2.4. Color Code:
Black, Red
3. Cable Assembly
3.1. Nominal Lay Length:
3.00” LHL (4.00 tw/ft)
4. Jacket
4.1. Material:
Plenum Rated PVC
4.2. Wall Thickness:
0.015”
4.3. Diameter:
0.148” ± 0.015”
4.4. Color:
Green
4.5. Ripcord:
Yes

4.6. Weight:
17 Lbs/Mft
5. Markings
5.1. Type:
Cable permanently identified via surface inkjet print
5.2. Print Legend:
CERCO CABLE WWW.CERCOCABLE.COM #B7560-4 E171202 18AWG 2C 75C (UL) CL3P OR FPLP OR C(UL)US CMP    FT6     "ROHS COMPLIANT"     MADE IN USA
5.3. Footage Markers:
Yes Ascending/Descending
6. Standards
6.1. Cable suitable for installation under NEC (NFPA 70) articles 800, 

6.2. Cable suitable for installation in Canada under Section 60 of CEC, Part I

6.3. C(UL)US listed as CMP per UL standard 444 and per CSA C22.2 No. 214-17
6.4. UL listed as CL3P per UL standard 13 or FPLP per UL standard 1424

6.5. Cable meets NFPA 262 (Steiner tunnel) flame test

6.6. Made in the USA
6.7. Due to the frequent updates to regulations, specifically California Proposition 65, EU REACH SVHCs and ROHS please contact Lake Cable for the most up to date compliance statement.
ALL SPECIFIED PARAMETERS WITHOUT A TOLERANCE ARE NOMINAL AND SUBJECT TO VERIFICATION. LAKE CABLE IS NOT RESPONSIBLE FOR UNKNOWN PERFORMANCE ATTRIBUTES THAT WERE NOT MADE KNOWN TO LAKE CABLE AT THE TIME OF DESIGN. 
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