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Specification Sheet
Lake Cable Part #: P184F-08
Description:
18 AWG 4 conductor solid bare copper wire with PVC insulation, unshielded and overall PVC jacket for low-voltage electronic cable applications
1. Conductor
1.1. AWG Size & Stranding:
18 AWG Solid 
1.2. Material:
Annealed Bare Copper
1.3. Conductor Count:
4 Conductors
2. Insulation
2.1. Material:

Polyvinylchloride
2.2. Wall Thickness:

0.009”
2.3. Diameter:

0.058” ± 0.002”
2.4. Color Code:

Black, Red, Brown, Blue
3. Cable Assembly
3.1. Lay Length:

3.00” LHL (4.00 Tw/FT), Nominal
4. Jacket
4.1. Material:

Polyvinylchloride
4.2. Wall Thickness:

0.015”
4.3. Diameter:

0.170” ± .015”
4.4. Color:


Grey
4.5. Ripcord:

Yes
4.6. Weight:


31 Lbs/Mft
5. Markings
5.1. Type:
Cable permanently identified via surface inkjet print
5.2. Legend: 

LAKE CABLE E171202 18AWG 4C 75C (UL) CL3P OR FPLP OR C(UL)US CMP   FT-6

"ROHS COMPLIANT"     MADE IN USA
5.3. Footage Markers:           Yes
5.4. Nominal Electrical Characteristics

5.5. Impedance:

62 Ω

5.6. Capacitance:

30 pF/ft.

5.7. Conductor DCR:

6.35 Ω/Mft. @ 20C Maximum
6. Standards
6.1. Cable suitable for installation under NEC (NFPA 70) articles 800, 725 and 760 guidelines

6.2. Cable suitable for installation in Canada under Section 60 of CEC, Part I
6.3. C(UL)US listed as CMP per UL standard 444 and per CSA C22.2 No. 214-17
6.4. UL listed as CL3P per UL standard 13 or FPLP per UL standard 1424

6.5. Cable meets NFPA 262 (Steiner tunnel) flame test
6.6. Cable meets RoHS 2002/95/EC Directive, RoHS 2 2011/65/EU Directive, RoHS 3 2015/863/EU Directive

6.7. Cable is REACH compliant per Regulation (EC) No 1907/2006 (240) Updated January 23, 2024

6.8. Made in the USA

6.9. [image: image1.png]


WARNING: This product may contain chemicals, such as Vinyl Chloride, known to the state of California to cause cancer. For more information, go to www.P65Warnings.ca.gov. Wash hands after handling
ALL SPECIFIED PARAMETERS WITHOUT A TOLERANCE ARE NOMINAL AND SUBJECT TO VERIFICATION. LAKE CABLE IS NOT RESPONSIBLE FOR UNKNOWN PERFORMANCE ATTRIBUTES THAT WERE NOT MADE KNOWN TO LAKE CABLE AT THE TIME OF DESIGN. 
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