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Specification Sheet
Lake Cable Part #: PFF242CST/X-08CERCO
	Your signature constitutes that you have read and agreed to this specification sheet and upon confirmation of your order; this item may be non-cancelable and non-returnable.
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Description:
24AWG 2 conductor 7 strand tinned copper wire, plenum rated Foam FEP insulation, shielded, with an overall plenum rated PVC jacket
1. Conductor
1.1. AWG Size & Stranding:
24AWG 7 Strands Class B
1.2. Material:

Annealed Tinned Copper
1.3. Conductor Count:
2 Conductors

2. Insulation
2.1. Material:

Plenum rated Foam FEP 
2.2. Wall Thickness:
0.016”
2.3. Diameter:

0.055” ± 0.002”
2.4. Color Code:

White & Blue/White
3. Assembly
3.1. Nominal Lay Length:
1.75” LHL (6.86 Tw/Ft)
3.2. Shield:
Aluminum/Mylar Tape – 100% Coverage (Foil Facing Out)


3.3. Drain Wire:

24 AWG 7 Strand Tinned Copper 

4. Jacket
4.1. Material:

Plenum Rated Polyvinylchloride
4.2. Wall Thickness:
0.015”
4.3. Diameter:

0.142” ± 0.015”
4.4. Color:


Gray
4.5. Ripcord:

Yes

4.6. Weight:

12 Lbs/Mft
5. Markings
5.1. Type:


Cable shall be permanently identified via surface inkjet print
5.2. Legend:

CERCO CABLE WWW.CERCOCABLE.COM #AG70-10 E171202 24AWG 2C SHIELDED 
75C (UL) CL3P OR FPLP OR C(UL)US CMP FT6 "ROHS COMPLIANT" MADE IN USA

5.3. Footage Markers:
Yes, Ascending/Descending 
6. Nominal Electricals Characteristics 
6.1. 
Impedance:

100 Ω 
6.2. Capacitance: 

12.5 pF/ft. 

6.3. DC Resistance: 

23.8 Ω/Mft. @ 20°C
7. Standards
7.1. Cable suitable for installation under NEC (NFPA 70) articles 800, 725 and 760 guidelines

7.2. Cable suitable for installation in Canada under Section 60 of CEC, Part I

7.3. C(UL)US listed as CMP per UL standard 444 and per CSA C22.2 No. 214-17

7.4. UL listed as CL3P per UL standard 13 or FPLP per UL standard 1424

7.5. Cable meets NFPA 262 (Steiner tunnel) flame test

7.6. Operating Voltage: 300V RMS
7.7. Operating Temperature -20°C to 75°C
7.8. Made in the USA

7.9. Due to the frequent updates to regulations, specifically California Proposition 65, EU REACH SVHCs and ROHS please contact Lake Cable for the most up to date compliance statement.

ALL SPECIFIED PARAMETERS WITHOUT A TOLERANCE ARE NOMINAL AND SUBJECT TO VERIFICATION. LAKE CABLE IS NOT RESPONSIBLE FOR UNKNOWN PERFORMANCE ATTRIBUTES THAT WERE NOT MADE KNOWN TO LAKE CABLE AT THE TIME OF DESIGN. 
*Client expressly indemnifies Lake Cable, LLC for any liabilities relating in any way to Lake Cable’s placement of markings on the product, when such markings are specified for such placement by the client
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"This document and the information contained in it are proprietary and confidential and may not be reproduced or disseminated, in whole or in part, without the prior written consent of Lake Cable, LLC (the “Company”).  Except to the extent expressly required or permitted by applicable law, any unauthorized reproduction or dissemination of this document or the information contained in it without the Lake Cable, LLC prior written consent is strictly prohibited.  This document remains the property of Lake Cable, LLC and must be returned to the Lake Cable, LLC upon request."
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